# Preface

## Document Overview

The EL10 is a versatile general-purpose inverter designed with a compact structure, featuring rich hardware and software configurations. It is characterized by its flexibility, ease of use, and reliability, primarily used for speed control of three-phase AC asynchronous motors. It is widely applied in industries such as food and beverage, logistics packaging, textiles, and woodworking machinery.

This manual provides detailed information on product communication, specifications, networking, and communication configuration.

## More Information

| Document Title | Content Summary |
| --- | --- |
| EL10 Series General Purpose Inverter Manual | This manual introduces installation, wiring, commissioning, and trial operation procedures, including installation dimensions, mechanical installation, electrical installation, commissioning and trial operation, fault handling, function code table, and peripheral electrical components. |
| EL10 Series General Purpose Inverter Communication Manual | Introduces product communication overview, specifications, networking, communication configuration, and other detailed content. |

## Version Change Record

| Revision Date | Release Version | Change Content |
| --- | --- | --- |
| 2024–8 | Ver 1.0 | First release of the manual. |

## About Obtaining the Manual

This manual is not shipped with the product. To obtain the electronic PDF version, you can do so through the following methods:

Log in to the Changsha Risheng Electric official website (www.cssunye.com), go to the “Download Center,” search for the keyword, and download.

## Warranty Statement

Under normal use, if the product malfunctions or is damaged, we provide warranty service within the warranty period. After the warranty period, repair fees will be charged.

Within the warranty period, product damage caused by the following situations will incur repair fees.

● Damage to the product caused by not operating it according to the specifications in the manual.

● Damage to the product caused by fire, water, or abnormal voltage.

● Damage to the product caused by using it for purposes other than its intended function.

● Damage to the product caused by using it beyond the specified operating range.

● Secondary damage to the product caused by irresistible forces (natural disasters, earthquakes, lightning strikes).

Service fees are calculated according to the manufacturer's uniform standards. In the event of a contract, the terms of the contract shall take precedence. For detailed warranty information, please refer to the 'Product Warranty Card'.

## Precautions

## Safety Statement

- This chapter provides safety precautions necessary for the correct use of this product. Before using this product, please read the user manual and correctly understand the information related to safety precautions. Failure to comply with the matters specified in the safety precautions may result in death, serious injury, or equipment damage.

- The 'Danger,' 'Warning,' and 'Caution' items in the manual do not represent all safety precautions, but are provided as a supplement to all safety precautions.

- This product should be used in an environment that meets the design specifications; otherwise, it may cause malfunctions. Any functional abnormalities or component damage caused by non-compliance with these specifications are not covered by the product's quality warranty.

- We will not assume any legal responsibility for personal injury, property damage, or other losses caused by non-compliance with the content of this manual or improper operation of the product.

## Safety Level Definition

In this manual, safety precautions are divided into the following two categories:

Danger: Hazards caused by not operating as required, which may result in serious injury or even death;

Caution: Hazards caused by not operating as required, which may result in moderate injury or minor injury, and equipment damage;

Please read this chapter carefully when installing, commissioning, and maintaining this system, and strictly follow the safety precautions required in this chapter. The company shall not be liable for any injuries or losses caused by non-compliance with the operating procedures.

## Safety Precautions

| Usage Phase | Safety Level | Matters |
| --- | --- | --- |
| Before Installation | Danger | If water ingress, missing parts, or damaged components are found when unpacking the control system, do not install! If the packing list does not match the actual items, do not install! |
|  | Caution | Handle the equipment with care during transportation; otherwise, there is a risk of damaging the equipment! Do not touch the components of the control system with your hands; otherwise, there is a risk of static damage! |
| During Installation | Danger | Only trained personnel with electrical knowledge and experience in electrical equipment should operate. Non-professionals are strictly prohibited from operating! |
|  | Caution | Do not allow wire ends or screws to fall into the driver; otherwise, it can cause damage to the driver! Install the driver in a place with minimal vibration and avoid direct sunlight. |
| When wiring | Danger | The installation must be carried out by a professional electrical engineer; otherwise, unexpected dangers may occur! Before wiring, ensure that the power supply is in a zero-energy state; otherwise, there is a risk of electric shock! Ground the inverter correctly and in accordance with standards; otherwise, there is a risk of electric shock! |
|  | Caution | Follow the steps specified in the ESD (Electrostatic Discharge) prevention measures and wear an ESD wrist strap when performing wiring and other operations to avoid damaging the equipment or internal circuits of the product. When wiring the control circuit, use double-stranded twisted shielded wire and connect the shielding layer to the grounding terminal of the product; otherwise, it may cause abnormal operation of the product. |
| Before Powering On | Danger | Before powering on, ensure that the product is installed correctly, the wiring is secure, and the motor installation allows for reoperation. Before powering on, ensure that the power supply meets the product requirements to avoid damaging the product or causing a disaster! Do not open the cabinet door or protective cover, touch any terminal, or dismantle any component or part of the product while it is powered, as this can result in electric shock! |
|  | Caution | The inverter must have its cover securely fastened before powering on; otherwise, it may cause an electric shock! Wire according to the connection methods provided in this manual; otherwise, accidents may occur! |
| After Powering On | Danger | Do not open the cover after powering on. Otherwise, there is a risk of electric shock! Do not touch any input or output terminals of the inverter. Otherwise, there is a risk of electric shock! |
|  | Caution | If parameter identification is required, be cautious of the danger of injury from the rotating motor, as it may cause an accident! Do not arbitrarily change the manufacturer's parameters of the inverter, as this may cause damage to the equipment! |
| In Operation | Danger | Non-professional technical personnel should not test signals while the equipment is in operation, as this may cause personal injury or equipment damage! Do not touch the cooling fan or discharge resistor to check the temperature, as this may cause burns! |
|  | Caution | While the inverter is in operation, avoid dropping any objects into the equipment, as this may cause damage to the equipment! Do not use contactors to control the start and stop of the driver, as this can cause equipment damage! |
| During maintenance | Danger | Do not perform maintenance or servicing of the inverter without professional training, as this can result in personal injury or equipment damage! Do not perform maintenance or servicing on the equipment while it is energized, as this can result in electric shock! Ensure that the input power to the inverter has been disconnected for at least 10 minutes before performing maintenance or servicing on the driver, to avoid injury from residual charges on the capacitors! All plug-in modules must be inserted or removed only when the power is off! After replacing the communication module, it is necessary to set and check the parameters. |

Contents

Chapter 1 Overview of Communication Protocols		1

Chapter 2 Modbus Communication		2

2.1 Communication Introduction		2

2.2 Hardware Configuration		2

2.3 RS485 Connection Topology		2

2.4 Communication Transmission Method		3

2.5 Communication Data Frame Structure		3

2.6 Related Parameters		5

2.7 Communication Parameter Addresses		7

Chapter 3 CANopen Communication		12

3.1 Communication Introduction		12

3.1.1 Communication Specifications		12

3.2 Hardware Configuration		12

3.2.1 Communication Port		12

3.2.2 Wiring Instructions		13

3.3 Communication Description		14

3.3.1 CANopen Communication Key Points		14

3.3.2 CANopen Communication Protocol		15

3.3.3 Subordinate Protocol		22

3.3.4 Custom Protocol One		32

3.3.5 Custom Protocol Two		37

3.3.6CiA 402		38

3.4 CANopen Control Inverter Function Debugging		40

3.4.1 CANopen Select CiA 402 Protocol		40

3.4.2 CANopen Select Inverter Manufacturer Custom Protocol		41

3.4.3 Analog AIO and DIO		42

- Overview of Communication Protocols

| Supported Communication Protocols | Communication Hardware | Model |
| --- | --- | --- |
| Modbus | EL10A/EL10B Series Inverter | EL10A/EL10B |
| CANopen Communication | EL10B Series Inverter | EL10B |

- Modbus Communication

  - 2.1 Introduction to Communication

The EL10 Series Inverter uses an RS485 communication interface to connect to a PC/PLC for communication, forming a single-master multiple-slave PC/PLC communication network. Each communication slave must have a unique slave address, with the address setting range being 1～254, and 0 being the broadcast communication address. Users can control slaves (inverters) centrally through the master (usually a PC or PLC), using the Modbus communication protocol to set inverter operation commands, modify and read parameters, and read inverter operating status and fault information.

The EL10 Series Inverter supports Modbus-ASCII and Modbus-RTU slave communication protocols, which are serial communication protocols that define the content and format of information transmitted in serial communications. If the slave device encounters an error while receiving information or cannot execute a command issued by the master, the slave will send a fault message to the master.

    - Communication Specifications

| Item |  | Content |
| --- | --- | --- |
| Communication Protocol |  | Modbus Protocol |
| Standard Specifications |  | Modbus-RTUSlave Communication Protocol |
| Topology |  | Bus Type |
| Maximum Communication Rate |  | 19.2Kbps |
| Slave Functions | Number of Request Messages that Can be Received Simultaneously | 1 |

    - Hardware Configuration

The communication module of the EL10A is integrated on the control board and is connected to the Modbus bus via a screw terminal block.

Fig. 2.1 Modbus Communication Terminals

Table 2-1 Terminal Pin Description

| Category | Terminal/DIP Switch Symbol | Terminal/DIP Switch Name | Function Description |
| --- | --- | --- | --- |
| Communication Interface | 485+ | 485 Communication Interface | 485 Signal Positive |
|  | 485- | 485 Communication Interface | 485 Signal Negative |
| GND | GND | Power Ground | Connects the reference ground for all 485 nodes |

  - RS485 Connection Topology

RS485 buses typically use a daisy chain topology, where the 485+ interfaces of the master and multiple slaves are connected in sequence, as are the 485- interfaces. The daisy chain RS485 bus topology is shown in Fig. 2-2. The daisy chain topology has advantages such as low signal reflection, high communication success rate, and no need for additional equipment. To reduce the impact of interference on the output signal, it is recommended to use shielded twisted pair cables for RS485 bus transmission.

Figure 2-2  Daisy Chain RS485 Bus Topology

  - Communication Transmission Method

The RS485 communication protocol supports both half-duplex and full-duplex modes. In most cases, we use the half-duplex mode, where at any given time, only one device (master or slave) can transmit data while the other can only receive data. The RS485 communication transmission method is shown in Figure 2-3. Data is transmitted in the form of messages as specified by the Modbus-RTU protocol. One frame of data is sent at a time, and when the idle time on the communication line exceeds the transmission time of 3.5 bytes, it indicates the start of a new communication frame.

Figure 2-3  RS485 Communication Transmission Method

The EL10 inverter is equipped with Modbus-RTU and Modbus-ASCII communication protocols, allowing users to choose which protocol to use. In the network, only one device (the master) can establish the protocol, that is, issue a “query/command.”Other devices (slaves) can only respond to the master’s “query/command” by providing data or performing operations as directed by the master. The master can be a PC, PLC, etc., and the slave refers to the inverter. The master can communicate independently with a specific slave or broadcast information to all slaves. When the master sends a “query/command,” the slave must return a response, but if the master sends a broadcast, the slaves do not need to respond.

  - Communication Data Frame Structure

The Modbus-RTU protocol communication data format is shown in Figure 2-4. The inverter only supports read or write operations for Word-type parameters, with the corresponding communication read command being 03; the write command being 06, and the multiple write command being 10. Byte or bit read/write operations are not supported.

Figure 2-4(a) Master Read Command Frame

Figure 2-4(b) Slave Read Response Frame

Note: Theoretically, the master can read multiple consecutive parameters at once (i.e., n can be up to 12), but it should be noted that it cannot exceed the last parameter of the current parameter group, otherwise, an error response will be returned.

Figure 2-4(c) Master Write Command Frame

Figure 2-4(d) Slave Write Response Frame

Figure 2-4(e) Master Station Multiple Write Command Frame

Note: Multiple write operations, like multiple reads, can only operate on up to 12 parameters.

Figure 2-4(f) Slave Station Multiple Write Response Frame

The read response error command for the slave station is 0x83, the write response error command is 0x86, the multiple write response error command is 0x90, and CRC check errors do not respond. Additionally, in the error types, 0x01 indicates a command code error, 0x02 indicates an address error, 0x03 indicates a data error, and 0x04 indicates an unprocessable command.

Figure 2-4(g) Slave Station Read Error Response Frame

Figure 2-4(h) Slave Station Write Error Response Frame

Figure 2-4(i) Slave Station Multiple Write Error Response Frame

  - Relevant Parameters

| Function Code | Name | Content | Default Value | Parameter Description |
| --- | --- | --- | --- | --- |
| F8-00 | Baud Rate Setting | 4.8～19.2 kb/s | 19.2 | Used to set the data transmission rate between the host computer and the inverter. The higher the baud rate, the faster the communication. Note: The baud rate set on the host computer and the inverter must be the same, otherwise communication cannot be performed. |
| F8-01 | Communication Data Format | 1：7,N,2 for ASCII 2：7,E,1 for ASCII 3：7,O,1 for ASCII 4：7,E,2 for ASCII 5：7,O,2 for ASCII 6：8,N,1 for ASCII 7：8,N,2 for ASCII 8：8,E,1 for ASCII 9：8,O,1 for ASCII 10：8,E,2 for ASCII 11：8,O,2 for ASCII 12：8,N,1 for RTU 13：8,N,2 for RTU 14：8,E,1 for RTU 15：8,O,1 for RTU 16：8,E,2 for RTU 17：8,O,2 for RTU | 12 | The data format set by the master device and the inverter must be consistent; otherwise, communication cannot be established. |
| F8-02 | Communication Address | 1～254 | 1 | Used to set the communication address of the inverter. |
| F8-03 | Response delay | 0.0～200.0ms | 2.0 | The intermediate interval time from the end of data reception by the inverter to the transmission of data to the higher-level machine. If the response delay is less than the system processing time, the response delay will be set to the system processing time; If the response delay is greater than the system processing time, the system will wait after processing the data until the response delay time is reached before sending data to the higher-level machine. |
| F8-04 | Communication timeout time | 0.0～100.0s | 0.0 | When this parameter is set to a non-zero value, if the interval between one communication and the next exceeds the communication timeout time, the system will report a Modbus transmission timeout (E058) fault. In most cases, it is set to zero, which means it is invalid. |

  - Communication Parameter Address

This section contains communication content used for controlling the inverter's operation, inverter status, and related parameter settings. R indicates read-only, and RW indicates read-write.

The parameter address is indicated by the function code group number and label:

High Byte: F0～FF groups are 0x00～0x0F, U0～U1 are 0x10～0x11, H1～H3 are 0x12～0x15, L0～L8 are 0x16～0x1E.

Low Byte: 0x00～0xFF

For example, the address F0-11 is represented as 0x000B

Caution:

FF group: Neither readable nor writable parameters;

U group: Read-only, not writable parameters.

Some parameters cannot be modified when the inverter is in operation; some parameters cannot be modified regardless of the inverter's state. When changing the function code parameters, also pay attention to the range, unit, and related descriptions of the parameters.

| Function Code Group Number | Communication Access Address |
| --- | --- |
| F0～FE Groups | 0x0000～0x0FFF |
| U0～U1 Groups | 0x1000～0x11FF |
| H1～H3 Groups | 0x1200～0x15FF |
| L0～L8 Groups | 0x1600～0x1EFF |

20xx Definition:

| Address | Parameter Description | Address | Parameter Description |
| --- | --- | --- | --- |
| 2102H | Set Frequency (Unit: 0.01Hz) | 2210H | DI Switch Status, Read-Only |
| 2103H | Output Frequency (Unit: 0.01Hz), Read-Only | 2211H | DO Switch Status, Read-Only |
| 2200H | Output Current (Unit: A), Read-Only | 2212H | Multi-Speed, Read-Only |
| 2201H | Count Value, Read-Only | 2213H | DI CPU Pin Status, Read-Only |
| 2202H | Actual Motor Speed (Unit: rpm), Read-Only | 2214H | DO CPU Pin Status, Read-Only |
| 2203H | Bus Voltage (Unit: V), Read-Only | 2215H | Reserved, Read-Only |
| 2204H | Output Voltage (Unit: V), Read-Only | 2216H | Pulse Input Frequency (Unit: Hz), Read-Only |
| 2205H | Power Factor Angle (Unit: deg), Read-Only | 2217H | Pulse Input Position, Read-Only |
| 2206H | Output Power (Unit: kW), Read-Only | 221AH | GFF Detection Percentage (Unit: %) |
| 2207H | Actual Feedback Speed (Unit: rpm), Read-Only | 221EH | User-Defined Display |
| 2208H | Output Torque (Unit: Nm), Read-Only | 2223H | Speed Mode, Read-Only |
| 2209H | Reserved, Read-Only | 2224H | Carrier Frequency (Unit: Hz), Read-Only |
| 220AH | PID Feedback Value, Read-Only | 222CH | Reserved, Read-Only |
| 220BH | AI1, Read-Only | 222DH | Reserved, Read-Only |
| 220CH | Reserved, Read-Only | 222EH | PID Setpoint, Read-Only |
| 220DH | Reserved, Read-Only | 222FH | PID compensation, read-only |
| 220EH | IGBT temperature (unit: ℃), read-only | 2230H | PID output frequency (unit: Hz), read-only |

Stop/Run parameter section:

| Type | Command Address | Command content |
| --- | --- | --- |
| Control command input （Write-only） | 2000H | xx12: Forward operation xx22: Reverse operation xx13: Forward jog xx23: Reverse jog xxx1: Stop operation |
| Set frequency (read/write) | 2001H | Set frequency (unit: 0.01Hz) |
| External signal (read/write) | 2002H | 0001: External Fault Signal 0002: Fault Reset Signal 0004: Base Fault Signal |
| Inverter Fault Address (Read-Only) | 2100H | xx01: Overcurrent During Acceleration xx33: External Interrupt xx02: Overcurrent During Deceleration xx34: Password Input Three Times Incorrect xx03: Overcurrent During Constant Speed xx36: Invalid Communication Command xx04: Reserved xx37: Invalid Communication Address xx05: Reserved xx38: Communication Data Error xx06: Reserved xx39: Communication Write to Read-Only Address xx07: Overvoltage During Acceleration xx3A: Modbus Transmission Timeout xx08: Overvoltage During Deceleration xx3E: Regenerative Braking During Deceleration xx09: Overvoltage during constant speed xx3F: Excessive slip xx0A: Overvoltage during stop xx40: Please reset machine code xx0B: Undervoltage during acceleration xx42: Software overcurrent xx0C: Undervoltage during deceleration xx45: Reserved xx0D: Undervoltage during constant speed xx46: Reserved xx0E: Undervoltage during stop xx48: Reserved xx0F: Input phase loss protection xx4C: Reserved xx10: IGBT temperature too high xx4D: Reserved xx11: Reserved xx4F: U-phase overcurrent xx15: Inverter overload xx50: V-phase overcurrent xx16: Motor 1 overload protection xx51:W Phase Overcurrent xx17:Reserved xx52:U Phase Output Phase Loss xx18:Motor Overheat PTC xx53:V Phase Output Phase Loss xx1A:Over Torque 1 xx54:W Phase Output Phase Loss xx1B:Reserved xx57:Low Frequency Overload Protection xx1C:Low Current xx65:CANopen Disconnection xx1D:Reserved xx66:CANopen Disconnection xx1F:Memory Read Error xx68:CANopen Hardware Disconnection xx21:Reserved xx69:CANopen Index Error xx22:Reserved xx6A:CANopen Station Number Error xx23: Reserved xx6B: CANopen Memory Error xx24: CC Hardware Circuit Abnormality xx78: Reserved xx25: OC Hardware Circuit Abnormality xx80: Over Torque 3 xx26: Reserved xx81: Over Torque 4 xx29: PID Disconnection xx87: Reserved xx2A: Reserved xx8D: Ground Fault Before Operation xx30: AI Current Signal Disconnection xx92: Reserved xx31: External Terminal Abnormality xx93: Reserved xx32: External Terminal Emergency Stop |
|  |  | 01xx: Communication Command Error 16xx: Motor Overheat 02xx: Communication Address Error 18xx: Over Slip 03xx: Communication Data Error 19xx: Reserved 04xx: Inverter cannot process 1Cxx: Output phase loss warning 05xx: Communication transmission timeout 1Exx: Different model copy error 07xx: Parameter copy error 1Fxx: Reserved 08xx: Parameter copy error 20xx: Reserved 09xx: IGBT overheating warning 24xx: CANopen software disconnect 0Bxx: PID feedback signal warning 25xx: CANopen software disconnect 0Cxx: AI current signal disconnect 27xx: CANopen hardware disconnect 0Dxx: Low current warning 28xx: CANopen index error 0Fxx: Reserved 29xx: CANopen station number error 11xx: Reserved 2Axx: CANopen Memory Error 12xx: Reserved 2Bxx: CANopen SDO Transfer Timeout 13xx: Input Phase Loss 2Cxx: CANopen SDO Receive Overflow 14xx: Over Torque 1 2Dxx: CANopen Initialization Error 15xx: Reserved 2Exx: CANopen Format Error |

60xx Definition

| Command Address | bit | Bit Name | Value | Parameter Description |
| --- | --- | --- | --- | --- |
| 6000h (RW) | 0 | CMD_ACT | 0 | fcmd =0 |
|  |  |  | 1 | fcmd = Fset(Fpid) |
|  | 1 | EXT_CMD1 | 0 | Forward Direction Command |
|  |  |  | 1 | Reverse Direction Command |
|  | 2 | - | - | - |
|  | 3 | HALT | 0 | Continue Running to Target Speed |
|  |  |  | 1 | Temporary Stop According to Deceleration Settings |
|  | 4 | LOCK | 0 | Continue Running to Target Speed |
|  |  |  | 1 | Maintain Current Frequency |
|  | 5 | JOG | 0 | JOG OFF |
|  |  |  | Pulse 1 | JOG RUN |
|  | 6 | QSTOP | 0 | None |
|  |  |  | 1 | Quick Stop |
|  | 7 | SERVO_ON | 0 | Servo OFF |
|  |  |  | 1 | Servo ON |
|  | 11~8 | GEAR | 0000 | Main Speed |
|  |  |  | 0001~ 1111 | 1~15 Segment Speed Frequency Switching |
|  | 13~12 | ACC/DEC | 00 | First Segment Acceleration/Deceleration Time |
|  |  |  | 01 | Second Segment Acceleration/Deceleration Time |
|  |  |  | 10 | Third Segment Acceleration/Deceleration Time |
|  |  |  | 11 | Fourth Segment Acceleration/Deceleration Time |
|  | 14 | EN_SW | 0 | Do Not Allow Multi-Segment Command and Acceleration/Deceleration Time Switching |
|  |  |  | 1 | Allow Multi-Segment Command and Acceleration/Deceleration Time Switching |
|  | 15 | RST | Pulse 1 | Clear Error Code |
| 6002h (RW) | 15-0 | Velocity Cmd |  | Frequency Command (0.01Hz) |
| 6100h (R) | 0 | ARRIVE | 0 | Frequency command not received |
|  |  |  | 1 | Frequency command received |
|  | 1 | DIR | 0 | Forward |
|  |  |  | 1 | Reverse |
|  | 2 | WARN | 0 | No warning |
|  |  |  | 1 | Warning occurred |
|  | 3 | ERROR | 0 | No error |
|  |  |  | 1 | Error occurred |
|  | 5 | JOG | 0 | None |
|  |  |  | 1 | On JOG |
|  | 6 | QSTOP | 0 | None |
|  |  |  | 1 | On Quick Stop |
|  | 7 | SERVO_ON | 0 | PWM OFF |
|  |  |  | 1 | PWM ON |
|  | 8 | Ready | 0 | Ready OFF |
|  |  |  | 1 | Ready ON |
|  | 15-9 | - | - | - |
| 6102h （R） | 15-0 | Velocity cmd |  | Actual Output Frequency |

- CANopen Communication

  - Communication Overview

    - Communication Specifications

| Item |  | Content |
| --- | --- | --- |
| Function Code Support | Function Code to Switch Node Address | Node Address Manually Set, Maximum 127, Cannot Be Automatically Assigned |
|  | Function Code to Switch Baud Rate | Baud Rate Manually Set, Cannot Be Automatically Assigned |
| Baud Rate | 20Kbps~1Mbps Baud Rate | 50Kbps, 100Kbps, 125Kbps, 250Kbps, 500Kbps, 1Mbps |
| SYNC | SYNC Consumer | Consumption Synchronization Signal |
| SDO | Initialization Upload/Download | Transmission of Data Less Than or Equal to 4 Bytes |
| PDO | Synchronous TPDO/RPDO | Synchronization Range 1~240, Default Only TPDO1 and RPDO1 Enabled, Configurable |
|  | Asynchronous TPDO/RPDO | Time-Triggered, Default Only TPDO1 and RPDO1 Enabled, Configurable |
| EMCY | Communication Emergency Message | Send Internal Error Code, See Section 3.5 |
| NMT | Bootup Service | Supports Startup Message Sending |
| NMTErrCtl | Life Guard | Optional Node Protection Function (Cannot Be Used with Heartbeat Production) |
|  | Heartbeat Consumer | Support Node Heartbeat Consumption |
|  | Heartbeat Producer | Support Node Heartbeat Production |
| Expert Mode | Configure PDO Communication Parameters and Mapping via Function Codes | Manually Configure PDO Communication Parameters and Mapping |

  - Hardware Configuration

    - Communication Port

The CAN communication module of the EL10B is integrated on the control board and connects to the CAN bus via a screw-type terminal block.

Figure 3.1 CANopen Communication Terminal

Table 3-2 Terminal Pin Description

| Category | Terminal/DIP Switch Symbol | Terminal/DIP Switch Name | Function Description |
| --- | --- | --- | --- |
| Communication Interface | CAN+ | CAN Communication Interface | CAN Signal Positive |
|  | CAN- | CAN Communication Interface | CAN Signal Negative |
| GND | GND | Power Ground | Connects the Reference Ground for All CAN Nodes |

Figure 3-2 CANopen Terminal Resistor DIP Switch

Table 3-3 DIP Switch Description

| DIP Switch Name | DIP Switch Position | Function Description |
| --- | --- | --- |
| CAN Termination Matching | ON | Perform Termination Resistor Matching |
|  | OFF | Do Not Perform Termination Resistor Matching |

    - Wiring Instructions

The wiring diagram for the CAN Bus is shown in Figure 3.3. The CAN Bus is recommended to use shielded twisted pair cables for connection. Terminal matching resistors should be connected at both ends of the CAN Bus. The DIP switches should be set according to the diagram on the terminal block. Failing to connect or connecting insufficient terminal resistors can affect communication quality, leading to unstable communication.

Figure 3.3 CAN Bus Wiring Diagram

  - Communication Instructions

    - Key Points for CANopen Communication

CANopen communication sub-protocol CiA 301 (DS 301) includes cyclic communication and event-triggered communication.

CANopen device sub-protocol defines direct access to inverter parameters and key process data.

The inverter's CANopen interface supports CiA 402 (DS 402, inverter and motion control sub-protocol) specifications and inverter manufacturer custom specifications.

The maximum transmission distance of CANopen is limited by the transmission speed; the higher the speed, the shorter the communication distance.

Theoretically, up to 127 communication nodes can be connected in a CAN network, but in practice, the number of nodes is limited by the transmission capability of the CAN transceiver.

Unless otherwise specified, the inverter is defined as a slave node (Server) in the CAN network.

Table 3-4 CANopen Protocol

| Application layer | CANopen Application layer | CiA 402 CiA 301 |
| --- | --- | --- |
| Presentation layer |  |  |
| Session layer |  |  |
| Transport layer |  |  |
| Network layer |  |  |
| Data link layer |  | CAN2.0A/B |
| Physical layer |  | ISO 11898 |

Table 3-5 CANopen Parameter Settings

| Name | Description | Default Value |
| --- | --- | --- |
| F8-07 Communication Decoding Method | Select manufacturer custom protocol, 0 indicates Custom Protocol One, 1 indicates Custom Protocol Two | 1 |
| F8-14 CANopen Node Address | Set the node address, each device in the same network must have a unique node address. 0: Disable CANopen slave, 1~127: Slave node address number, a CAN network supports up to 127 slave nodes. | 0 |
| F8-15 CAN Bus Communication Rate | User selects the CANopen communication rate, all devices in the same network must use the same communication rate. | 0 |
| F8-18 CANopen Warning Record | Displays the inverter's CANopen warning information | Read-only |
| F8-19 CiA 402 Protocol Selection | Used to select the CiA 402 protocol and the inverter manufacturer's custom protocol for CANopen index parsing. 0: Inverter manufacturer's custom protocol, 1: CiA 402 protocol | 0 |
| F8-20 CANopen Communication Status | Display Inverter CANopen Node Status | Read-only |
| F8-21 CiA402 Operation Status | Display Inverter Motor Operation Status | Read-only |
| F8-22 CANopen Index Reset | CANopen Index Data Clear Command | 0xFFFF |

    - CANopen Communication Protocol

CANopen Communication Protocol includes NMT (Network Management Object), SYNC (Synchronous Object), SDO (Service Data Object), PDO (Process Data Object, including transmitted TPDO, Tx PDO and received RPDO, Rx PDO, transmission and reception are referenced to the CANopen node itself), EMCY (Emergency Object).

Table 3-6 Communication Protocol

| Communication Object | Function Code (binary) | COB-ID(hex) |
| --- | --- | --- |
| NMT | 0000 | 00 |
| SYNC | 0001 | 80 |
| EMCY | 0001 | 81 ... FF |
| TPDO1 | 0011 | 181 ... 1FF |
| RPDO1 | 0100 | 201 ... 27F |
| TPDO2 | 0101 | 281 ... 2FF |
| RPDO2 | 0110 | 301 ... 37F |
| TPDO3 | 0111 | 381 ... 3FF |
| RPDO3 | 1000 | 401 ... 47F |
| TPDO4 | 1001 | 481 ... 4FF |
| RPDO4 | 1010 | 501 ... 57F |
| TSDO | 1011 | 581 ... 5FF |
| RSDO | 1100 | 601 ... 67F |

The COB-ID encoding format is as follows:

Table 3-7 COB-ID (CAN Object ID, 11 or 29 bits)

| Function Code |  |  |  | Node ID |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |

      - NMT

NMT follows the Master/Slave protocol model, where the NMT master can unconditionally control the state transitions of the slave. NMT management involves six states from the start of power-up of a CANopen node, including initialization, application layer reset, communication reset, pre-operation mode, operation mode, and stop mode. The NMT message corresponds to a CAN communication data frame with a length of 2 bytes, and the ID field is 0.

Table 3-8 NMT messages

| ID field | Data field (Byte 0) | Data field (Byte 1) |
| --- | --- | --- |
| 0 | NMT CMD | Node ID |

If Node ID is 0, it indicates all NMT broadcast frames, and all slave stations will respond. The NMT CMD list is as follows:

Table 3-9 NMT CMD

| NMT CMD | Meaning |
| --- | --- |
| 01h | Start remote node |
| 02h | Stop remote node |
| 80h | Enter pre-operation mode |
| 81h | Node reset |
| 82h | Communication reset |

The list of node statuses is as follows:

Table 3-10 Node Statuses

| Node Status Word | Meaning |
| --- | --- |
| 00h | Boot-up |
| 04h | Stopped State |
| 05h | Operational Mode |
| FFh | Pre-Operation Mode |

The CANopen state machine is as follows:

Figure 3-4 CANopen State Machine

The effective operating states of each communication protocol object are listed in the following table:

Table 3-11 Effective Operating States

|  | Initialization | Pre-Operation Mode | Operational Mode | Stopped State |
| --- | --- | --- | --- | --- |
| PDO | \ | \ | Active | \ |
| SDO | \ | Active | Active | \ |
| SYNC | \ | Active | Active | \ |
| EMCY | \ | Active | Active | \ |
| NMT | \ | Active | Active | Active |
| Boot-up | Active | \ | \ | \ |

      - SDO

SDO follows the Client/Server protocol model, used for transmitting data with non-string time requirements (parameter settings), data length 0~4Byte. Common SDO protocol is Fast SDO (SDO command byte bit1 set to 1 indicates Fast SDO), which means all data is transmitted during initialization (initial SDO upload/download). If the transmission length is greater than 4Byte, Fast SDO cannot be used, and standard SDO must be used for segmented transmission. The Object Dictionary is a group object of the CANopen node, each node has its own Object Dictionary, which contains multiple parameters, and the parameters describe the supported parameter attributes and values. SDO accesses the device Object Dictionary through index and sub-index, each object has a single index value, and a single index can have multiple sub-index values. The SDO data frame format is as follows:

Table 3-12 SDO Data Frame Format

| SDO Data Frame Analysis |  |  |  | SDO CMD Analysis |  |
| --- | --- | --- | --- | --- | --- |
| data byte num | Comment |  |  | bit num | Comment |
| byte0 | SDO CMD |  |  | bit0 | size |
| byte1 | SDO Index Low Byte |  |  | bit1 | expedited |
| byte2 | SDO Index High Byte |  |  | bit2 | SDO Unused Byte Count |
| byte3 | SDO sub-index |  |  | bit3 |  |
| byte4 | SDO data low word low byte | When SDO status inquiry is performed from client to server, these 4 bytes are invalid |  | bit4 | \ |
| byte5 | SDO data low word high byte |  |  | bit5 | cmd 1: init download (issue parameters) 2: init upload (status inquiry) 3: stop SDO transfer |
| byte6 | SDO data high word low byte |  |  | bit6 |  |
| byte7 | SDO data high word high byte |  |  | bit7 |  |

      - PDO

PDO follows the Producer/Consumer protocol model, where each network node can receive information from the transmitting node and can also determine whether to process the received information, used for transmitting time-critical process data (reference values, control commands, status information, etc.), allowing for one-to-one or one-to-many data transmission. PDO transmission can be initiated through an internal timer (asynchronous communication), upon receiving a synchronization frame (synchronous communication), and via remote requests. The CAN interface supports up to 8 PDOs (including 4 TPDOs and 4 RPDOs), with only TPDO1 and RPDO1 enabled by default. Multiple application objects can be transmitted in a single PDO frame through PDO mapping. PDO object mapping can only be modified when the node is in Pre-Operation Mode.

PDO mapping format CANopen object mapping value is hexadecimal encoding, PDO mapping data format is as follows:

Table 3-13 PDO Mapping Data Format

| Type | MSB |  | LSB |
| --- | --- | --- | --- |
| UINT32 | 31 16 | 15 8 | 7 0 |
| Description | Index (e.g., 6040h) | Sub-Index (e.g., 02h) | Object bit length (e.g., 10h corresponds to 16 bits, 08h corresponds to 8 bits) |

Note:

- PDO mapping sub-index starts from 1.

- If the PDO mapping input value is 0, the mapping of the current sub-index and all subsequent sub-indices will be ignored.

The relationship between PDO transmission type settings and transmission methods is as follows:

Table 3-14 PDO Transmission Type

| Transmission type setting value | Cyclic | Non-cyclic | Synchronous | Asynchronous | Remote Request |
| --- | --- | --- | --- | --- | --- |
| 0 | \ | Active | Active | \ | \ |
| 1~240 | Active | \ | Active | \ | \ |
| 252 | \ | \ | Active | \ | Active |
| 253 | \ | \ | \ | Active | Active |
| 255 | \ | \ | \ | Active | \ |

A transmission type value of 0 indicates that two PDOs transmit synchronous non-cyclic information (currently unsupported). A transmission type value of 1~240 indicates the number of SYNCs between two PDO transmissions. A transmission type value of 252 indicates that data is updated immediately after receiving SYNC (currently unsupported). A transmission type value of 253 indicates that data is updated immediately after receiving RTR (currently unsupported). A transmission type value of 255 indicates asynchronous non-cyclic transmission.

PDO Mapping Configuration via SDO This section provides an example of configuring the slave PDO mapping via the CANopen master SDO. Refer to this example for other PDO configurations. The slave PDO configuration is as follows:

- Node ID = 1;

- RPDO1 : 6040h Control Word, 6042h Target Speed;

- TPDO1 : 6041h Status Word, 6043h Actual Target Speed;

- TPDO1 is sent to the master station at a 100ms cycle.

In the pre-operation mode of the CANopen slave node, the object configuration is as shown in the following table: RPDO1 mapping configuration steps:

Table 3-15 RPDO1 Mapping Configuration Steps

| Step | Index (hex) | sub-Index (hex) | Name | Write Value （hex） | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | 1400 | 01 | RPDO1 Parameter: COB-ID | 80000201 | Disable RPDO1 |
| 2 | 1400 | 02 | RPDO1 Parameter: Transmission Type | FF | Transmission Type 255 |
| 3 | 1600 | 00 | RPDO1 Mapping: Number of Entries | 0 | Write 0 Before Mapping Configuration |
| 4 | 1600 | 01 | RPDO1 Mapping: Mapping Object 1 | 60400010 | 6040h Control Word, Sub-index 00, Data Length 16 bits |
| 5 | 1600 | 02 | RPDO1 Mapping: Mapping Object 2 | 60420010 | 6042h Target Speed, Sub-index 00, Data Length 16 bits |
| 6 | 1600 | 00 | RPDO1 Mapping: Number of Entries | 2 | Map 2 Objects |
| 7 | 1400 | 01 | RPDO1 Parameter: COB-ID | 201 | Enable RPDO1 |

TPDO1 Mapping Configuration Steps:

Table 3-16 TPDO1 Mapping Configuration Steps

| Step | Index (hex) | sub-Index (hex) | Name | Write Value （hex） | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | 1800 | 01 | TPDO1 Parameter: COB-ID | 80000181 | Disable TPDO1 |
| 2 | 1800 | 02 | TPDO1 Parameter: Transmission Type | 1 | Transmission Type 1 |
| 3 | 1800 | 05 | TPDO1 Parameter: Event Timer | 64 | 100ms |
| 4 | 1A00 | 00 | TPDO1 Mapping: Number of Entries | 0 | Write 0 Before Mapping Configuration |
| 5 | 1A00 | 01 | TPDO1 Mapping: Mapping Object 1 | 60410010 | 6041h Status Word, Subindex 00, Data Length 16 bits |
| 6 | 1A00 | 02 | TPDO1 Mapping: Mapping Object 2 | 60430010 | 6043h Actual Target Speed, Subindex 00, Data Length 16 bits |
| 7 | 1A00 | 00 | TPDO1 Mapping: Number of Entries | 2 | Map 2 Objects |
| 8 | 1800 | 01 | TPDO1 Parameter: COB-ID | 181 | Enable TPDO1 |

      - EMCY

The emergency object is triggered when an internal fault occurs in the CANopen device, informing the CANopen master of the fault code via an emergency frame. The emergency frame is a diagnostic message and does not affect CANopen communication. Refer to 6.5 CANopen Fault Codes for CANopen fault codes.

    - Sub-Protocol

The sub-protocol specifies the meaning of parameters, control words, status words, and variable values (reference values and actual values) transmitted and received via the CAN bus. The inverter supports two sub-protocols:

CiA 402. The inverter internally converts the CiA 402 protocol. The inverter does not use the CiA 402 protocol by default.

Manufacturer-specific protocol. Two manufacturer-specific protocols, Protocol One (F8-07=0) and Protocol Two (F8-07=1), can both allow the inverter to operate in speed mode.

The selection of sub-protocol standards can be achieved through parameter F8-19.

Figure 3-5 Communication Sub-Protocol

The CANopen control index definitions supported by the inverter are as follows:

Table 3-17 CANopen Control Index

| CANopen Protocol Standard Selection | Speed Mode |  |
| --- | --- | --- |
|  | index-subindex | Meaning |
| CiA402 | 6042-0x00 | Target Speed (rpm) |
| Midea Protocol One | 2020-0x02 | Target Frequency (Hz) |
| Midea Protocol Two | 2060-0x03 | Target Frequency (Hz) |

General indexes do not require sub-protocol selection and can be used universally, relevant indexes are as follows:

- Indexes with read-only (RO) attributes.

- Parameter group read/write indexes (0x2010-0x01 ~ 0x201F-0x64, 0x2070-0x01 ~ 0x20B0-0x64)

- Acceleration/deceleration time setting indexes (604F-0x00, 6050-0x00)

      - Sub-protocol Introduction

The CiA 402 Protocol is a CANopen application layer protocol specifically designed for inverters and motion control scenarios, built upon the CiA 301 Protocol. The inverter is divided into 9 operating states, including Start, Initialization (Not ready to switch on), Not Running (Switch on disable), Ready to Run (Ready to switch on), Running (Switch on), Operation Enabled (Operate enable), Quick Stop Active, Fault Reaction Active, and Fault. After the inverter is powered on and completes initialization, it will remain in the Ready to Run state. The inverter can only be controlled to run when it is in the normal operating state.

Figure 3-6 Inverter State Machine

Caution: When the set value of Index 605A is 5~7, the inverter can be controlled to return directly from fast shutdown to operational enable by disabling the fast shutdown and control commands. Otherwise, the inverter cannot return directly from fast shutdown to operational enable.

Table 3-18 Control Word (Index 6040h)

| bits | 15~9 | 8 | 7 | 6~4 | 3 | 2 | 1 | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Meaning | Reserved | Halt | Fault Reset | Normal Operation | Operational Enable | Fast Shutdown | Enable Voltage | Running |

Note: To start the motor, first send 0xxxx110 (06h) to enter the Ready to Switch ON state, and then send 0xxxx111 (07h) to enter the Switch ON state, at which point the motor will start rotating.

Table 3-19Status Word (Index 6041h)

| bits | 15~14 | 13~12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Meaning | Reserved | Normal Operation | Amplitude Limiting Action | Reach Target Value | Remote Control | Reserved | Warning | Disable Operation | Fast Shutdown | Voltage Enable | Fault | Operation Enable | Running | Operation Preparation Complete |

CANopen Object Dictionary

Table 3-20 Standard Object Dictionary (Object Dictionary)

| Index | Object |
| --- | --- |
| 0000h | Reserved |
| 0001h ~ 025Fh | Data Types (Data types) |
| 0260h ~ 0FFFh | Reserved |
| 1000h ~ 1FFFh | Communication Profile Area |
| 2000h ~ 5FFFh | Manufacturer-Specific Profile Area |
| 6000h ~ 9FFFh | Standardized Profile Area |
| A000h ~ AFFFh | Standardized Network Variable Area (Compliant with IEC61131-3) |
| B000h ~ BFFFh | Standardized System Variable Area for Routing Gateway |
| C000h ~ FFFFh | Reserved |

Table 3-21 Communication Profile Area

| Index (hex) | sub-Index (hex) | Name | Data Format | Read/Write | Meaning |
| --- | --- | --- | --- | --- | --- |
| 1000 | 0 | Device Type | unsigned 32 | RO | Device Type Description |
| 1001 | 0 | Fault Register | unsigned 8 | RO | Describe fault types, refer to the fault register description table below for details |
| 1005 | 0 | Synchronous message COB-ID | unsigned 32 | RW | Synchronous message COB-ID for synchronized transmission |
| 1006 | 0 | Synchronous communication cycle period | unsigned 32 | RW | Set synchronous communication cycle period (us) |
| 100C | 0 | Watchdog time | unsigned 16 | RW | Watchdog time (ms) * Lifetime Factor = Node Watchdog Protocol Lifetime |
| 100D | 0 | Lifetime Factor | unsigned 8 | RW | Watchdog time (ms) * Lifetime Factor = Node Watchdog Protocol Lifetime |
| 1010 | 1 | Save parameters | unsigned 32 | RW | Write SDO value 0x65766173 (“evas”) to save all parameters |
|  | 2 |  |  |  | Write SDO value 0x65766173 (“evas”) to save communication parameters (index 0x1000~0x1FFF) |
| 1011 | 1 | Restore Default Parameters | unsigned 32 | RW | Write SDO value 0x64616F6C (“daol”) to restore all parameters to default values |
|  | 2 |  |  |  | Write SDO value 0x64616F6C (“daol”) to restore communication parameters (index 0x1000~0x1FFF) to default values |
| 1014 | 0 | Emergency Message COB-ID | unsigned 32 | RW | Define Emergency Object (EMCY) COB-ID, default value: 0x80 + Node-ID |
| 1016 | 1 | Consumer Heartbeat Time | unsigned 32 | RW | Value definition: bits 31 ~ 24 reserved, bits 23 ~ 16 Node-ID, bits 15 ~ 0 heartbeat time (ms) |
| 1017 | 0 | Producer Heartbeat Time | unsigned 32 | RW | Define heartbeat cycle time (ms), write 0 to disable heartbeat function |
| 1018 | 1 | Vendor ID | unsigned 32 | RO | Vendor ID, inverter manufacturer value: 0x476 (for temporary use) |
|  | 2 | Product Code |  |  | Product Code |
|  | 3 | Version Number |  |  | Version Number |
| 1400 | 0 | RPDO1 Communication Parameters | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x200 + Node-ID |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
| 1401 | 0 | RPDO2 Communication Parameters | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000300 + Node-ID (RPDO2 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
| 1402 | 0 | RPDO3 Communication Parameters | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000400 + Node-ID (RPDO3 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
| 1403 | 0 | RPDO4 Communication Parameters | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000500 + Node-ID (RPDO4 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
| 1600 | 0 | RPDO1 Mapping Parameters | unsigned 8 | RO | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default Value: 0x60400010, 0x6040-0x00 Indicates 16-bit Control Word in CiA 402 Protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW | Default Value: 0x60420010, 0x6042-0x00 Indicates 16-bit Status Word in CiA 402 Protocol |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1601 | 0 | RPDO2 Mapping Parameters | unsigned 8 | RO | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default Value: 0x20264110, 0x2026-0x41 Indicates 16-bit DO Status Setting in Custom Protocol One |
|  | 2 | Mapping Object 2 | unsigned 32 | RW |  |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1602 | 0 | RPDO3 Mapping Parameters | unsigned 8 | RO | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default Value: 0x60400010, 0x6040 Indicates 16-bit Control Word in CiA 402 Protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW |  |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1603 | 0 | RPDO4 Mapping Parameter | unsigned 8 | RO | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default Value: 0x60400010, 0x6040 Indicates 16-bit Control Word in CiA 402 Protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW |  |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1800 | 0 | TPDO1 Communication Parameter | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x180 + Node-ID |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
|  | 3 | Inhibition Time | unsigned 8 | RW | PDO Transmission Minimum Interval, Default Value:0 (Not Used) |
|  | 5 | Event Timer | unsigned 8 | RW | Default Value:0 (Not Used) |
| 1801 | 0 | TPDO2 Communication Parameter | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000280 + Node-ID (TPDO2 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
|  | 3 | Inhibition Time | unsigned 8 | RW | PDO Transmission Minimum Interval, Default Value:0 (Not Used) |
|  | 5 | Event Timer | unsigned 8 | RW | Default Value:0 (Not Used) |
| 1802 | 0 | TPDO3 Communication Parameter | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000380 + Node-ID (TPDO3 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
|  | 3 | Inhibition Time | unsigned 8 | RW | PDO Transmission Minimum Interval, Default Value:0 (Not Used) |
|  | 5 | Event Timer | unsigned 8 | RW | Default Value:0 (Not Used) |
| 1803 | 0 | TPDO4 Communication Parameter | unsigned 8 | RO | Maximum Supported Sub-index Number |
|  | 1 | COB-ID | unsigned 32 | RW | Default Value:0x80000480 + Node-ID (TPDO4 Disabled) |
|  | 2 | Transmission Type | unsigned 8 | RW | Default Value:5 |
|  | 3 | Inhibition Time | unsigned 8 | RW | PDO Transmission Minimum Interval, Default Value:0 (Not Used) |
|  | 5 | Event Timer | unsigned 8 | RW | Default Value:0 (Not Used) |
| 1A00 | 0 | TPDO1 Mapping Parameter | unsigned 8 | RW | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default value: 0x60410010, 0x6041-0x00 represents the 16-bit status word in the CiA 402 protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW | Default value: 0x60430010, 0x6043-0x00 represents the 16-bit real-time target speed (rpm) in the CiA 402 protocol |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1A01 | 0 | TPDO2 Mapping Parameters | unsigned 8 | RW | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default value: 0x20260110, 0x2026-0x01 represents the 16-bit DI terminal status in Custom Protocol One |
|  | 2 | Mapping Object 2 | unsigned 32 | RW | Default value: 0x20266110, 0x2026-0x61 represents the 16-bit AI ratio value in Custom Protocol One |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1A02 | 0 | TPDO3 Mapping Parameters | unsigned 8 | RW | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default value: 0x60410010, 0x6041-0x00 represents the 16-bit status word in the CiA 402 protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW |  |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |
| 1A03 | 0 | TPDO4 Mapping Parameters | unsigned 8 | RW | Number of Mapping Objects (0~4) |
|  | 1 | Mapping Object 1 | unsigned 32 | RW | Default value: 0x60410010, 0x6041-0x00 represents the 16-bit status word in the CiA 402 protocol |
|  | 2 | Mapping Object 2 | unsigned 32 | RW |  |
|  | 3 | Mapping Object 3 | unsigned 32 | RW |  |
|  | 4 | Mapping Object 4 | unsigned 32 | RW |  |

Table 3-22 Fault Register Description

| Bit | Description |
| --- | --- |
| 0 | General Fault |
| 1 | Current |
| 2 | Voltage |
| 3 | Temperature |
| 4 | Communication Fault |
| 5 | Device Protocol Specification |
| 6 | Reserved |
| 7 | Manufacturer Specified |

    - Custom Protocol One

Table 3-23 Custom Protocol One

| Index | Sub-Index | R/W | Data Format | Meaning |
| --- | --- | --- | --- | --- |
| 0x2010+PrGroupNum 0x2070+PrGroupNum-0xE | PrNum+1 | R/W | unsigned 16 | Inverter Parameter Setting and Reading※ |
| 0x2020 | 0x01 | R/W | unsigned 16 | Control Command Word |
|  | 0x02 | R/W | unsigned 16 | Frequency Command (0.01Hz) |
|  | 0x03 | R/W | unsigned 16 | Trigger Command |
| 0x2021 | 0x01 | R | unsigned 16 | Hbyte: Warn Code Lbyte: Error Code |
|  | 0x02 |  |  | Inverter Operating Status |
|  | 0x03 |  |  | Frequency Command (0.01Hz) |
|  | 0x04 |  |  | Output Frequency (0.01Hz) |
|  | 0x05 |  |  | Output Current (0.1A) |
|  | 0x06 |  |  | DC Bus Voltage (0.1V) |
|  | 0x07 |  |  | Output Voltage (0.1V) |
|  | 0x08 |  |  | Current Multi-Segment Speed Command Segment Number |
|  | 0x09 |  |  | Reserved |
|  | 0x0A |  |  | Display Count Value |
|  | 0x0B |  |  | Output Power Factor Angle (0.1°) |
|  | 0x0D |  |  | Actual Motor Speed (rpm) |
|  | 0x10 |  |  | Output Power (0.001kWh) |
|  | 0x11 |  |  | Parameter Group Number |
|  | 0x13 |  |  | Firmware Version (highword) |
| 0x2022 | 0x01 | R | unsigned 16 | Output Current (0.01A), when current is greater than 655.36A, the decimal place automatically switches to 1 |
|  | 0x02 |  |  | Display Count Value |
|  | 0x03 |  |  | Output Frequency (0.01Hz) |
|  | 0x04 |  |  | DC Bus Voltage (0.1V) |
|  | 0x05 |  |  | Output Voltage (0.1V) |
|  | 0x06 |  |  | Output Power Factor Angle (0.1°) |
|  | 0x07 |  |  | Three-Phase Output Power (kW) |
|  | 0x08 |  |  | Actual Motor Speed (rpm) |
|  | 0x09 |  |  | Output Torque (0.1%) |
|  | 0x0B |  |  | After PID function is activated, display PID feedback value (0.01%) |
|  | 0x0C |  |  | AI Terminal Input Value (0-100%) |
|  | 0x0F |  |  | Power Module IGBT Temperature (0.1℃) |
|  | 0x11 |  |  | Digital Terminal Input Mode Selection (F5—15) |
|  | 0x12 |  |  | Digital Terminal Output Mode Direction (F6—04) |
|  | 0x13 |  |  | Current Multi-Segment Speed Command Segment Number |
|  | 0x14 |  |  | Digital Terminal Input Status (1: on) |
|  | 0x15 |  |  | Digital Terminal Output Status (1: on) |
|  | 0x1A |  |  | Overload Count (0.00-100.00%) |
|  | 0x1C |  |  | DC Bus Voltage (0.1V) |
|  | 0x1F |  |  | User Physical Quantity Output |
|  | 0x20 |  |  | Actual Output Frequency Gain Coefficient (0.01) |
|  | 0x25 |  |  | Inverter Carrier Frequency (kHz) |
|  | 0x27 |  |  | Inverter Status |
|  | 0x2A |  |  | Energy Display (0.1kWh) |
|  | 0x2F |  |  | PID Reference Target (0.01%) |
|  | 0x30 |  |  | PID Offset (0.01%) |
|  | 0x31 |  |  | PID Output Frequency (0.01Hz) |
| 0x2026 | 0x01 | R | unsigned 16 | DI Terminal Input Status |
|  | 0x03-0x40 | R | \ | Reserved |
|  | 0x41 | R/W | unsigned 16 | DO Terminal Output Status |
|  | 0x42-0x60 | R |  | Reserved |
|  | 0x61 | R |  | AI Ratio Value |
|  | 0x64-0x6A | R |  | Reserved |

※: Note the mapping relationship between the Object Dictionary and the inverter function codes is as follows:

Object Dictionary Index = 0x2010 + Function Code Group Number (F0-FF Function Group);

or 0x2070 + Function Code Group Number (U0-L8 Function Group)

Object Dictionary Sub-index = Function Code Group Internal Offset in Hexadecimal + 1;

Table 3-24 Control Command Word Bit Definitions:

| Control Command Word |  |
| --- | --- |
| bit 1-0 | 0: No function |
|  | 1: Stop |
|  | 2: Start |
|  | 3: JOG Start |
| bit 3-2 | Reserved |
| bit 5-4 | 0: No function |
|  | 1: Forward Command |
|  | 2: Reverse Command |
|  | 3: Change Direction |
| bit 7-6 | 0: First Segment Acceleration/Deceleration |
|  | 1: Second Segment Acceleration/Deceleration |
|  | 2: Third Segment Acceleration/Deceleration |
|  | 3: Fourth Segment Acceleration/Deceleration |
| bit 11-8 | 0: Main Speed |
|  | 1-15: First to Fifteenth Segment Speed Selection |
| bit 12 | 1: Enable bit 6-11 Function |
| bit 15-13 | Reserved |

Table 3-25 Trigger Command Word Bit Definition

| Trigger Command |  |
| --- | --- |
| bit 0 | 1: External Fault (EF) |
| bit 1 | 1: Reset Command |
| bit 2 | 1: External Interrupt (BB) |
| bit 15-3 | Reserved |

Table 3-26 Inverter Operation Status Word Bit Definitions

| Inverter Operating Status |  |
| --- | --- |
| bit 1-0 | 0: Stopped |
|  | 1: Accelerating |
|  | 2: Standby |
| bit 2 | JOG Operation |
| bit 4-3 | 0: Forward |
|  | 1: Reverse to Forward |
|  | 2: Forward to Reverse |
|  | 3: Reverse |
| bit 7-5 | Reserved |
| bit 8 | 1: Main frequency source is communication interface |
| bit 9 | 1: Main frequency source is analog signal input |
| bit 10 | 1: Main command source is communication interface |
| bit 11 | 1: Parameter Lock |
| bit 12 | 1: Enable Keypad Parameter Copy Function |
| bit 15-13 | Reserved |

Table 3-27 Inverter Status Word Bit Definitions

| Inverter Status |  |
| --- | --- |
| bit 1-0 | 0: No Direction |
|  | 1: Forward |
|  | 2: Reverse |
| bit 3-2 | 0: Inverter Ready |
|  | 1: Inverter Fault |
| bit 4 | 1: Inverter Has Output 0: No Output |
| bit 5 | 1: Warning Present 0: No Warning |

For the mapping relationship between terminal inputs/outputs and CANopen index, refer to 6.4.3 CANopen Analog AIO and DIO Description.

    - Custom Protocol Two

Table 3-28 Custom Protocol Two

| Index | Sub-Index | R/W | Data Format | Bit Definitions |  | Speed Mode |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Bit | Meaning |  |
| 0x2060 | 0x01 | R/W | unsigned 16 | 0 | Ack | 0: fcmd = 0 1: fcmd = fset |
|  |  |  |  | 1 | Dir | 0: Forward Command 1: Reverse Command |
|  |  |  |  | 2 | Move | \ |
|  |  |  |  | 3 | Halt | 0: Continue Running to Target Speed 1: Temporarily Stop According to Deceleration Settings |
|  |  |  |  | 4 | Hold | 0: Continue Running to Target Speed 1: Maintain Current Frequency |
|  |  |  |  | 5 | JOG | 0: OFF 1: RUN |
|  |  |  |  | 6 | Qstop | Fast Shutdown |
|  |  |  |  | 7 | RUN | 0: Shutdown 1: Startup |
|  |  |  |  | 8 | Multi-Speed Selection Bit | Multi-Speed Selection Bit 1 |
|  |  |  |  | 9 |  | Multi-speed Selection Bit 2 |
|  |  |  |  | 10 |  | Multi-speed Selection Bit 3 |
|  |  |  |  | 11 |  | Multi-speed Selection Bit 4 |
|  |  |  |  | 12 | Acceleration/Deceleration Time Selection Bit | Acceleration/Deceleration Time Selection Bit 1 |
|  |  |  |  | 13 |  | Acceleration/Deceleration Time Selection Bit 2 |
|  |  |  |  | 14 | Software Terminal Function Enable | Software Multi-speed and Acceleration/Deceleration Time Switch Enable |
|  |  |  |  | 15 | Reset | Clear Fault Codes |
|  | 0x02 |  |  | 0-15 | Run Mode CMD 0: Speed Mode | 0: Speed Mode |
|  | 0x03 |  |  | 0-15 | Frequency Command | Frequency Command (0.01Hz) |
|  | 0x05 |  | signed 32 | 0-31 | Reserved | \ |
|  | 0x06 |  | unsigned 16 | 0-15 | Reserved | \ |
|  | 0x07 |  | signed 16 | 0-15 | Reserved | \ |
|  | 0x08 |  | unsigned 16 | 0-15 | Reserved | \ |
| 0x2061 | 0x01 | R | unsigned 16 | 0 | Arrive | Frequency command received |
|  |  |  |  | 1 | Dir | 0: Forward 1: Reverse |
|  |  |  |  | 2 | Warn | Warning Occurred |
|  |  |  |  | 3 | Error | Fault Occurred |
|  |  |  |  | 4 | Reserved | Reserved |
|  |  |  |  | 5 | JOG | JOG Operation |
|  |  |  |  | 6 | Qstop | Fast Shutdown |
|  |  |  |  | 7 | PowerOn | Excitation |
|  |  |  |  | 15-8 | Reserved | Reserved |
|  | 0x02 |  |  | 0-15 | Reserved | Reserved |
|  | 0x03 |  |  | 0-15 | Frequency | Actual Output Frequency |
|  | 0x04 |  |  | 0-15 | Reserved | Reserved |
|  | 0x05 |  | signed 32 | 0-31 | Reserved | Reserved |
|  | 0x06 |  | unsigned 16 | 0-15 | Reserved | Reserved |

    - CiA 402

Table 3-29 Supported CiA 402 Index

| Index | Sub-Index | Definition | Default Value | R/W | Data Format | Unit | PDO Mapping |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0x6007 | 00h | Communication Abnormal Action Selection | 2 | R/W | signed 16 | \ | Yes |
| 0x603F | 00h | CANopen Fault Code | 0 | RO | unsigned 16 | \ | Yes |
| 0x6040 | 00h | Control Word | 0 | R/W | unsigned 16 | \ | Yes |
| 0x6041 | 00h | Status Word | 0 | RO | unsigned 16 | \ | Yes |
| 0x6042 | 00h | Target Speed (vl) | 0 | R/W | signed 16 | rpm | Yes |
| 0x6043 | 00h | Actual Target Speed (vl) | 0 | RO | signed 16 | rpm | Yes |
| 0x6044 | 00h | Actual Speed (vl) | 0 | RO | signed 16 | rpm | Yes |
| 0x604F | 00h | First Acceleration Time (vl) | 10000 | R/W | unsigned 32 | ms | Yes |
| 0x6050 | 00h | First Deceleration Time (vl) | 10000 | R/W | unsigned 32 | ms | Yes |
| 0x6051 | 00h | Rapid Stop Time (vl) | 0 | R/W | unsigned 32 | ms | Yes |
| 0x605A | 00h | Rapid Stop Option | 2 | R/W | signed 16 | \ | No |
| 0x605C | 00h | Stop Option | 1 | R/W | signed 16 | \ | No |
| 0x 6075 | 00h | Motor Rated Current (tq) | 0 | RO | unsigned 32 | mA | No |
| 0x 6078 | 00h | Actual Current Value (tq) | 0 | RO | signed 16 | 0.1%* | No |
| 0x 6079 | 00h | DC Bus Voltage (tq) | 0 | RO | unsigned 32 | mV | Yes |

*: Motor rated value is 100%

Control Word (6040h-00h) bit definitions are as follows:

| 15 11 |  |  |  |  | 10 | 9 | 8 | 7 | 6 4 |  |  | 3 | 2 | 1 | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ms |  |  |  |  | r | oms | h | fr | oms |  |  | eo | qs | ev | so |
| MSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LSB |

Note: ms = manufacture-specific; r = reserved; oms = operation mode specific; h = halt;

fr = fault reset; eo = enable operation; qs = quick stop; ev = enable voltage; so = switch on

Status Word (6041h-00h) bit definitions are as follows:

| 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ms |  | oms |  | ila | tr | rm | ms | w | sod | qs | ve | f | oe | so | rtso |
| MSB |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LSB |

Note: ms = manufacture-specific; oms = operation mode specific; lia = internal limit active; tr = target reached; rm = remote; w = warning; sod = switch on disable; qs = quick stop;

ve = voltage enable; f = fault; oe = operation enable; so = switch on; rtso = ready to switch on

The status word encoding mapping table is as follows:

Table 3-30 Status Word Encoding Mapping Table

| statusword | PDS FSA state |
| --- | --- |
| xxxx xxxx x0xx 0000b | Not ready to switch on |
| xxxx xxxx x1xx 0000b | Switch no disable |
| xxxx xxxx x01x 0001b | Ready to switch on |
| xxxx xxxx x01x 0011b | Switched on |
| xxxx xxxx x01x 0111b | Operation enable |
| xxxx xxxx x00x 0111b | Quick stop active |
| xxxx xxxx x0xx 1111b | Fault reaction active |
| xxxx xxxx x0xx 1000b | Fault |

  - CANopen control inverter function debugging

The preparation for controlling the inverter through CANopen is as follows:

- Wiring, refer to 6.2.2 CAN wiring method

- Set the frequency command source, parameter F0-06 = 6, select the frequency command source as CANopen setting.

- Set the operation command source, parameter F0-05 = 3, select the operation command source as CANopen setting.

- Set the CANopen slave node address, parameter F8-14 sets the slave address (default value is 0, indicating the slave function is disabled, 1~127 are valid slave node addresses). After setting the slave node address, if a station number error or CANopen memory error is reported, the CANopen can be reset by setting parameter F0-18 = 7.

- Set the CAN communication speed, parameter F8-15 sets the CANopen communication speed, parameter value setting range 0 (1Mbps), 1 (500kbps), 2 (250kbps), 3 (125kbps), 4 (100kbps), 5 (50kbps).

- The master station controls the slave station to enter the operational mode through NMT.

    - CANopen selects the CiA 402 protocol.

Speed mode is supported under the CiA 402 protocol. Parameter F8-19 = 1 enables the CiA 402 protocol. To enable the fast shutdown function using external terminals, set one of the parameters F5-00~F5-03 to 53.

The debugging steps are as follows:

  - Set the operation mode at index 6060h-00h to 2, setting the inverter to speed mode.

  - Control command words control the inverter to enter the operational enable state; send the control command word 0x0E at index 6040h-00h, then send 0x0F to enable the inverter to enter the operational enable state. Note the control of command word bits 6~4, defined as follows:

Table 3-31 Control command word bits 6~4

| bit 6 | bit 5 | bit 4 | Function |
| --- | --- | --- | --- |
| 1 | 0 | 1 | Run at the current frequency |
| 1 | 1 | 1 | Run to target |
| x | x | x | Decelerate to 0Hz |

  - Set the target speed, set the target speed at index 6042h-00h, the unit is rpm, a positive value indicates forward rotation, and a negative value indicates reverse rotation. Note the relationship between motor speed and frequency (information on the number of motor pole pairs).

  - Set the acceleration and deceleration time, set the inverter acceleration and deceleration time at index 604Fh-00h and 6050h-00h, the unit is ms.

  - Get the current operating speed, read the current operating speed at index 6043h-00h, the unit is rpm.

    - CANopen selects the inverter manufacturer's custom protocol.

Parameter F8-19 = 0 enables the inverter manufacturer's custom protocol.

      - Custom Protocol One

Custom Protocol One only supports speed mode. Debugging steps are as follows:

  - Parameter F8-07 = 0 enables Custom Protocol One.

  - Set the target frequency, index 2020h-02 sets the target frequency, the unit is 0.01Hz, for example, 5000 represents 50Hz.

  - Operation control, index 2020h-01h set to 2 indicates operation, index 2020h-01h set to 1 indicates stop.

      - Custom Protocol One

Custom Protocol Two supports speed mode. Debugging steps are as follows:

  - Parameter F8-07 = 1 enables Custom Protocol Two.

  - Set the target frequency, index 2060h-03 sets the target frequency, the unit is 0.01Hz, for example, 5000 represents 50Hz.

  - Operation control, set index 2060h-01h to 80h for excitation, set index 2060h-01h to 81h for operation.

    - Analog AIO and DIO

The inverter can simulate the status of IO ports through CANopen data, achieving software simulation of DO (Digital output) function, and can obtain the status of AI (Analog input) and DI (Digital input) and send it to the CAN Bus. CANopen index mapping for DIO (Digital input and output) and AIO (Analog input and output) is as follows: DI terminal (physical terminal name MI, Multi-function input) and CANopen index (2026h-01h) data bit mapping table:

Table 3-32 DI Terminal to CANopen Index Data Bit Mapping Table

| Terminal Name | Attribute | bit |
| --- | --- | --- |
| FWD | RO | bit 0 |
| REV | RO | bit 1 |
| MI 1 | RO | bit 2 |
| MI 2 | RO | bit 3 |
| MI 3 | RO | bit 4 |
| MI 4 | RO | bit 5 |

DO Terminal (Physical Terminal Name MO, Multi-function Output) to CANopen Index (2026h-41h) Data Bit Mapping Table:

Table 3-33 DO Terminal to CANopen Index Data Bit Mapping Table

| Terminal Name | Parameter Setting | Attribute | bit |
| --- | --- | --- | --- |
| RY 1 | F6-00 = 50 | RW | bit 0 |

AI Terminal (Physical Terminal Name AI, Analog Input) to CANopen Index (2026h) Data Bit Mapping Table:

Table 3-34 AI Terminal to CANopen Index Data Bit Mapping Table

| Terminal Name | Attribute | sub-index |
| --- | --- | --- |
| AI | RO | 61h |

  - CANopen Fault Code

Fault codes can be read through object 0x603F, and fault types can be read through object 0x1001. Fault codes xx80h~xxFFh and FF00h~FFFFh are manufacturer-defined.

Table 3-35 CANopen Fault Codes

| Fault Code | Meaning |
| --- | --- |
| 2213h | Overcurrent during acceleration and deceleration |
| 2240h | Ground fault |
| 2250h | Short circuit fault |
| 2310h | Continuous overcurrent |
| 2314h | Overcurrent at constant speed |
| 2331h | U phase output missing |
| 2332h | V Phase Output Missing |
| 2333h | W Phase Output Missing |
| 3130h | Input Phase Missing |
| 3210h | DC Bus Overvoltage |
| 3220h | DC Bus Undervoltage |
| 3330h | Motor Connection Switching Error |
| 4310h | Inverter Overtemperature |
| 5530h | EEPROM Abnormal |
| 7500h | Modbus Communication Fault |
| 8100h | CANopen software fault |
| 8130h | CANopen communication timeout |
| 8140h | CANopen disconnection |
| 8321h | Undercurrent |
| 8A00h | Low frequency overload protection |
| 9000h | External trigger fault |
| FF00h | IGBT temperature detection abnormal (th1o) |
| FF01h | Capacitor temperature detection abnormal (th2o) |
| FF04h | U phase current detection error (cd1) |
| FF05h | V Phase Current Detection Error (cd2) |
| FF06h | W Phase Current Detection Error (cd3) |
| FF07h | cbc Hardware Circuit Abnormal (hd0) |
| FF08h | oc Hardware Circuit Abnormal (hd1) |
| FF20h | Motor Overheat (oh3) |
| FF22h | PID Feedback Disconnection |
| FF25h | AI Disconnection (ACE) |
| FF26h | Password Input Three Times Incorrect (Pcod) |
| FF2Bh | Pre-Operation U Phase Short Circuit Detected (Aoc) |
| FF2Ch | V phase short circuit detected before operation (boc) |
| FF2Dh | W phase short circuit detected before operation (coc) |
| FF30h | Abnormality detected in S1 internal circuit (STL1) |
| FF32h | Abnormality detected in S2 internal circuit (STL2) |
| FF33h | Abnormality detected in internal circuit (STL3) |

Fault type data bit definitions are as follows:

| bit | Meaning |
| --- | --- |
| 0 | General Fault |
| 1 | Current |
| 2 | Voltage |
| 3 | Temperature |
| 4 | Communication Fault |
| 5 | Sub-protocol specified by the device |
| 6 | Reserved |
| 7 | Manufacturer Specified |

  - Communication configuration

For example, to establish CANopen communication between a configuration module and a PLC. The configuration process varies for different PLC models; please consult technical support for details.

    - Configuration settings

- Create project

Double-click to open the programming software for the upper computer, and click “New Project”. Select the PLC device type and programming language, change the save path and project name, then click “OK”.

Enter the “Network Configuration” interface, click the PLC icon, and check “CANopen Master”.

- Install EDS file

If the EDS file has not been installed before, it needs to be installed first. Enter the “Network Configuration” interface, click “Import EDS File”, find the path where the EDS file is stored, and click “Open”.

After the EDS file is successfully installed, you can find the CANopen device in the network device list — CANopen port — third-party manufacturer — SUYNE.

- Configure Slave

In the network device list, find the CANopen module, double-click to add the module.

In the “Device” list, under “CANopen”, find the module device, double-click to enter the configuration interface. In the “Slave Parameter Configuration” page, check “Enable Expert Mode” to open more configuration items.

The 'Slave Parameter Configuration' page can be used to configure the Node ID, which must match the setting in the inverter F8-14.

The 'CANopen Master' page can be used to configure the Baud Rate, which must match the setting in the inverter F8-15.

    - Configure Cyclic Communication

- Configure RPDO

EL10 supports 4 RPDO transmissions, with a maximum of 16 register data transmissions.

- Configure TPDO

EL10 supports 4 TPDO transmissions, with a maximum of 16 register data transmissions.

After configuration is complete, download the configuration, and the PLC and EL10 will automatically perform cyclic data exchange.

    - Configure Aperiodic Communication

- SDO Read Operation

EL10 supports the fast SDO transfer mechanism, with each data transmission length ranging from 0~4 bytes. The SDO_READ4 function block in the PLC can achieve SDO read operations.

- SDO write operation

The SDO_WRITE4 function block of the PLC can achieve SDO write operation.

- Appendix: General Periodic Fault Codes

| Diagnostic Classification | Status Code |
| --- | --- |
| Inverter Body Diagnostic Information (Register Address: 0x2100) | Low Byte (Fault Error Code): 0 No abnormal record 1 Overcurrent during acceleration (ocA) 2 Overcurrent during deceleration (ocd) 3 Overcurrent during constant speed operation (ocn) 6 Overcurrent during stop (ocS) 7 Overvoltage during acceleration (ovA) 8 Overvoltage during deceleration (ovd) 9 Overvoltage during constant speed operation (ovn) 10 Overvoltage during stop (ovS) 11 Low Voltage During Acceleration (LvA) 12 Low Voltage During Deceleration (Lvd) 13 Low Voltage During Constant Speed (Lvn) 14 Low Voltage During Stop (LvS) 15 Input Phase Loss Protection (OrP) 16 IGBT Overtemperature (oH1) 21 Inverter Overload (oL) 22 Motor Overload Protection (EoL) 24 Motor Overheat (oH3) 26 Over Torque 1 (ot1) 28 Low Current (uC) 31 Abnormal Memory Read (cF2) 36 cc Hardware Circuit Abnormal (Hd0) 37 oc Hardware Circuit Abnormal (Hd1) 41 PID Disconnection ACI (AFE) 48 ACI Disconnection (ACE) 49 External Terminal Abnormality (EF) 50 External Terminal Emergency Stop (EF1) 51 External Interrupt (bb) 52 Password Input Three Times Incorrect (Pcod) 54 Invalid Communication Command (CE1); 55 Invalid Communication Address (CE2) 56 Communication Data Value Error (CE3) 57 Communication Write to Read-Only Address (CE4) 58 Modbus Transmission Timeout (CE10) 62 Regenerative Braking Energy Action (dEb) 63 Excessive Slip (oSL) 79 U Phase Short Circuit Detected Before Operation (Aoc) 80 V Phase Short Circuit Detected Before Operation (boc) 81 W phase short circuit detected before operation (coc) 82 U phase output missing (oPL1) 83 V phase output missing (oPL2) 84 W phase output missing (oPL3) 87 Low frequency overload protection (oL3) 101 CANopen disconnection (CGdE) 102 CANopen disconnection (CHbE) 104 CANopen hardware disconnection (CbFE) 105 CANopen index error (CIdE) 106 CANopen station number error (CAdE) 107 CANopen memory error (CFrE) 141 Abnormal current detected before operation (b4GFF). High byte (Warn warning code): 0 No abnormal record 1 Communication error (CE1) 2 Communication Address Error (CE2) 3 Communication Data Error (CE3) 4 Inverter Cannot Process (CE4) 5 Communication Transmission Timeout (CE10) 7 Parameter Copy Error (SE1) 8 Parameter Copy Error (SE2) 9 IGBT Overheat Warning (oH1) 11 PID Feedback Signal Warning (PID) 12 ACI Current Signal Disconnection (AnL) 13 Low Current Warning (uC) 19 Input Phase Loss (PHL) 20 Over Torque (ot1) 22 Motor Overheat (oH3) 24 Over Slip (oSL) 28 Output Phase Loss Warning (OPHL) 30 Parameter copy error for different models (SE3) 36 CANopen software disconnection (CGdn) 37 CANopen software disconnection (CHbn) 39 CANopen hardware disconnection (CbFn) 40 CANopen index error (CIdn) 41 CANopen node address error (CAdn) 42 CANopen memory error (CFrn) 44 CANopen SDO receive overflow (CSbn) 46 CANopen format error (CPtn). |